Section 23 31 00

# PART-1	KITCHEN HOOD (TYPE 1) EXHAUST GREASE DUCT

1:1	SCOPE

- Option 1:  Provide single wall or double wall factory-built grease duct that is tested, listed and labeled by the Underwriters’ Laboratories, Inc. (UL 1978) for use with commercial cooking equipment, as described in NFPA-96.  Double wall duct shall be rated for reduced clearances to combustibles as per the manufacturer’s UL listing.

- Option 2: Provide double wall factory-built grease duct that is tested, listed and labeled by the Underwriters’ Laboratories, Inc (UL 1978 and UL 2221).  The UL listed grease duct shall be rated for zero clearance to combustibles, per UL 2221, and with an integral 2-hour fire-rating (ie: a shaft alternative).  Any hourly rated floor/wall penetrations are to be met with the use of factory provided firestops or an approved 3rd party engineered firestop system.

- Option 3: If the duct routing through a building permits, UL 1978 listed grease duct may be used in combination with UL 2221 listed grease duct (zero clearance and 2-hour fire rated).

1:2	  CONSTRUCTION

- Option 1: the single wall or double wall exhaust duct (UL 1978 listed only) shall have a 304 stainless steel inner wall (20 gauge min) and an aluminized steel outer wall jacket (double wall at 24 gauge min). The materials and construction of the modular sections and accessories shall be as specified by the terms of the product’s UL listing:

- Single wall (Model N) and/or:

- Double wall (Model IVSI-C1) using 1” thick high temperature body soluble fiber insulation between the duct walls and/or:

- Double wall (Model IVSI-C2) using 2” thick high temperature body soluble fiber insulation between the duct walls.

Option 2: the double wall exhaust duct (UL 1978 & UL 2221 listed) shall have a 304 stainless steel inner wall (20 gauge min) and an aluminized steel outer wall jacket (24 gauge min). The materials and construction of the modular sections and accessories shall be as specified by the terms of the product’s UL listing:

- Double wall (Model IVSI-Z3) using 3” thick high temperature body soluble fiber insulation between the duct walls.

- Aluminized steel surfaces exposed to the elements shall be field-painted by a minimum of one base coat of primer and one finish coat of corrosion resistant paint suitable for outer jacket skin temperatures of the given application as published by the duct manufacturer. Alternatively, an outer jacket constructed of 304 or 316 stainless steel (24 gauge min) may also be considered in lieu of painting.

- This exhaust system shall be designed and installed to be liquid tight and thus prevent leakage of grease and/or grease laden vapors into a building.

- Common duct sections & fittings (ie; lengths/elbows/tees) shall have a self-centering sleeve to ensure proper alignment at the inner wall joint connection.

- Inner duct joints shall be securely connected and sealed with factory supplied over-lapping V-bands and appropriate sealant as specified in the manufacturer’s installation instructions.  Double wall outer joints, exposed to weather, shall also be caulked per the installation instructions.

- Each system shall be designed, including local code requirements, to provide access for inspection and cleaning, permit drainage of grease residue through a duct section, enable the system to allow for the thermal expansion (as necessary) and if locally required, allow various types of fire suppression equipment and access to be integrated into the grease duct.

# PART-2	EXECUTION

2:1	INSTALLATION

- The prefabricated exhaust duct system shall be installed according to the manufacturer’s installation instructions, clearances to combustibles, factory submittal drawing, and shall conform to all applicable state and local codes.

- When installed according to the manufacturer’s installation instructions, the exhaust duct is permitted to be installed at a 1/16” per foot slope (<75 ft straight duct run) per duct manufacturer’s UL 1978 listing.  For a straight duct run >75 ft, the permitted slope is 3/16” per foot.

- Provide all modular straight sections, fittings, supports, guides, access doors, expansion joints, roof thimbles, roof flashings, and terminations as required to provide a complete system per the manufacturer’s recommended design and installation instructions.

- The entire exhaust system from the kitchen hood outlet (round outlet preferred) to the termination point, including all accessories, except as noted, shall be from one manufacturer.

- The termination shall comply to local code termination requirements.

- Roof penetrations shall be suitable for the specified roof construction and shall comply with the manufacturer’s installation instructions.

# PART-3	WARRANTY

3:1   WARRANTY

- The exhaust duct system shall have a limited lifetime warranty against functional failure due to defects in material and manufacturer’s workmanship from the date of installation.

- The manufacturer shall provide “to scale” drawings depicting the actual layout. The exhaust system shall be installed as designed by the manufacturer and in accordance with the terms of the manufacturer’s warranty and in conjunction with sound engineering practices.

# PART-4	PRODUCTS

  - MANUFACTURERS

- Product specification requirements shall be met by using AMPCO series exhaust grease duct as approved by the engineer. Equivalent submittals shall specify manufacturer’s model number, and other pertinent identification, and attest that the alternate material is in compliance with all specification requirements.

END OF SECTION 23 31 00